## Earth Resistance Demo Sheet
Earth Resistance Measurement Input Sheet-For DEMO
Title | ○○Electric Equipment Modification Work (Electrical Equipment Work) | [6 empty] | Groud Types
Site place | Ueda, Nagano, 386-1111, Japan | [6 empty] | Type | Criterion
Measurement Date | 2020-09-10 | [6 empty] | Class A | 10 | Ωor less
Temperature/Humidity | 26℃ |  | 50%rh | Weather |  | Cloudy |  | Class B | 55 | Ωor less |  | as per calculations
Measured by | Name |  |  | Inspected by |  | Name |  | Class C | 10 | Ωor less | 500 | Ωor less*
Instrument name | Earth Tester | [6 empty] | Class D | 100 | Ωor less | 500 | Ωor less
Model | FT6031-50 |  |  | Serial number |  | XXXXYYYZZ |  | *with ground-fault interrupter that trips within 0.5 sec.
Manufactured date | 2020-06-01 |  |  | Calibrated date |  | 2020-06-01
Manufacturer name | HIOKI E.E CORPORATION
Location | Type | Ref. Value |  | Measuremet Target | Measurement Value (Ω) |  | Judge ment
Cubical A Block | Class A | 10 | Ωor less | HV equipment A | 5.5 | Ohm | Pass
| Class D | 100 | Ωor less | LV equipment B | 101 | Ohm | Fail
| Class A | 10 | Ωor less | Ligthning Arrester | 2.5 | Ohm | Pass
| Class D | 100 | Ωor less | LV equipment C | 66.4 | Ohm | Pass
| Class B | 55 | Ωor less | Transformer secondary side | 56 | Ohm | Fail
| Class C | 10 | Ωor less | LV equipment B(400V) | 3.2 | Ohm | Pass |  |  | HIOKI disclaims any and all responsibility for any consequences arising out of use of this template.
Cubical B Block |  | #N/A | #N/A |  |  |  | #N/A
|  | #N/A | #N/A |  |  |  | #N/A
|  | #N/A | #N/A |  |  |  | #N/A
|  | #N/A | #N/A |  |  |  | #N/A
Street light-B Block |  | #N/A | #N/A |  |  |  | #N/A
|  | #N/A | #N/A |  |  |  | #N/A
|  | #N/A | #N/A |  |  |  | #N/A
|  | #N/A | #N/A |  |  |  | #N/A
Groud Types | Criterion
Class A | 10 | Ωor less
Class B | 55 | Ωor less |  | as per calculations
Class C | 10 | Ωor less | 500 | Ωor less* | *with ground-fault interrupter that trips within 0.5 sec.
Class D | 100 | Ωor less | 500 | Ωor less*